## Slide 1: Power network in large area detectors
Eric Heine, Nikhef KM3NeT power coordinator,
on the behalf of the KM3NeT collaboration

## Slide 2: Contents
KM3NeT Research Infrastructure
Site floor networks
Technical aspects of a large area power network:
  AC vs DC
  Conversions
  Load behavior
  Grounding
  Fuse regime
  On/Off procedures
Status implementation KM3NeT power networks
Acknowledgements

## Slide 3: KM3NeT Research Infrastructure
KM3NeT-Fr, coast of Toulon, 38 km, 2500 m
KM3NeT-It, Capo Passero, Sicily, 100 km, 3500 m
KM3NeT-Gr, Pylos <30 km, 3000 < 5000 m

## Slide 4: KM3NeT-Fr Network
10 W / DOM, 1000 W / ESS
Phase 1; 7 kW from shore
38 km from shore,
2500 m depth

## Slide 5: KM3NeT-It Network
100 km from shore,
3500 m depth
100 m
10 W / DOM, 15 W / floor
Phase 1; 9 kW from shore

## Slide 6: Technical aspects
Proven technology
Cost effective
Simple
Reliable
Flexible
AC vs DC
Conversions
  AC/DC
  Voltage level
Load behavior
  DC loads
  Constant power
Grounding
Fuse regime
On/Off procedures

## Slide 7: AC - DC
War of currents
1850 - 1900
Nikola Tesla
Thomas Edison
Some cities continued to use DC well into the 20th century. In central Helsinki, there was a DC network in existence up until the late 1940s, and in the 1960s, Stockholm's dwindling DC network was eliminated.
George Westinghouse
https://en.wikipedia.org/wiki/War_of_Currents
220-240 V at 50 Hz became the standard in Europe.
DC
AC

## Slide 8: AC or DC in long cables
Load
AC concept
PFC
Load
DC concept
Losses
AC cable : (Iload+ ICrms)2 (R+ jwL) + ICrms2 /jwC
Skin effect, proximity effect
DC cable : Iload2R
Isolation
Cable isolation depends on peak voltage: Upeak=Uac √2=Udc
P=Iac·Uac=Idc·Udc
A DC cable can transfer √2 more power.
e.g. Transfer efficiency @ 6.5 kW off shore, 3.5 kV on shore
  AC: 33%, DC: 96% @ 100 km cable
  AC: 85%, DC: 98% @ 38 km cable
E.Heine, H.Z.Peek, “Power distribution”, 2003; 2003 http://www.vlvnt,nl/proceedings/

## Slide 9: Main Electro Optical Cable
Fibers
Stainless steel tube
2 layers steel wire strands + water blocking compound
conductor of welded copper
HDPE diam. 17 mm
metal tape with overlap
PE sheath for additional abrasion and fish bite protection diam. 27.5 mm
Alcatel OALC xx 27mm LWP (light weight protected)
KM3NeT-Fr KM3NeT-It
OALC 7 OALC 3
36 Fibre 20
4 kV 10
AC type DC
38 km 100
R = 0.7 Ω/km cable
L= 0.4 mH/km cable
C= 180 nF/km cable
N.B. One wire + sea return

## Slide 10: AC – DC conversion
Classic
dilivered
power
current
voltage
PFC
delivered power
current
voltage
C
C
control
I
U
~200kHz
Classic:
more harmonic noise
higher I²R losses (3 x)
PFC (Power Factor Correction)
constant power load
voltage and current in phase

## Slide 11: DC – DC conversion
transformer isolated converter
control
~200kHz
+
-
+
-
boost converter
control
~200kHz
+
-
+
-
input circuit
switching circuit
rectifying circuit
output circuit
Use:
KM3NeT-It KM3NeT-Fr
Shore-subea 10kVdc 4kVac
To detection unit 375Vdc 400Vac
Detection unit 375Vdc 375Vdc
Sensor 12Vdc 12Vdc
http://www.emersonnetworkpower.com/en-US/Brands/Netsure/ensys-400v-dc/Pages/400v-dc-technology.aspx
400V DC Microgrid Small Scale Demo System for Telecom and Datacom Applications, VICOR, Presented at INTELEC 2012

## Slide 12: Load behavior
transformer isolated converter
control
~200kHz
+
-
+
-
feed back
Stablized voltage output ≈ constant power load
Network voltage↓=Network current↑=Cable loss↑
V0 = source voltage [V]
V1 = load voltage [V]
P0 = source power [W]
P1 = load power [W]
I = current [A]
L = length of connection [m]
r = connection resistance [Ω/m]
Vn> ½V0]
P1
V1
Vn
Pn
I1
L1
Vn+1
Pn+1
In
Ln
[V]
source
load

## Slide 13: Grounding
Prevent any circuit from a floating situation
ESD
isolation
Use one (1) low ohmic grounding point
e.g. 100 Ohm at source side
Avoid ground currents
electrolytic corrosion effects
signal/noise ratio

## Slide 14: Fuse regime
Main purpose: Prevent fault propagation
Base
DOM
DOM
DU
18x
JB
MVC
= fuse
̴
̴
̴
̴
̴
̴
̴
̴
̴
̴

## Slide 15: Status
KM3NeT-Fr
  Caclulation model
  Start up
  Shore station components
  Node design
Status KM3NeT-It
  Calculation model
  Progress in situ
  Power components
  Junction box design
Detection unit
  VEOC DC/DC converter

## Slide 16: KM3NeT-Fr

## Slide 17: Start - up
Time
Increasing shore voltage to keep node output constant
After timeout automatic switch on

## Slide 18: Power Feed Station
Thermo-magnetic circuit breaker
Thermo-magnetic circuit breaker
3 air conditioning 230V, 15kW
Variable power 54kVA
230V / 1 033 V – 3 720 V
Thermo-magnetic circuit breaker
Self
Lighting 230V, 500W
Thermo-magnetic circuit breaker
Thermo-magnetic circuit breaker
Thermo-magnetic circuit breaker
Adjustable compensation inductance
From 1,1H to 1,47H
Self.
Seabed network1
Seabed network 2
Micvar 3kW
Micvar 3kW
Outlets
(phone, computer, …) 230V, 16A
Presently we have 3 x 30kVA modules
We can supply one full node
Main grid
Battery
UPS
HV transf.

## Slide 19: Node progress

## Slide 20: KM3NeT-It
Preleminary
cable lengths

## Slide 21: Junction Box design
Rosanna Cocimano

## Slide 22: Power components
400 V to 12, 5, 3V3
<50 W
400 V, 2 A breaker
Angelo Orlando

## Slide 23: Progress
MVC, deployed and working
New CTF production
Proto tower deployed and working

## Slide 24: VEOC DC/DC converter
400 V to 12 V
2 – 15 W
4000 V isolation in/out
70 mmø x 30 mm
In oil up to 60 MPa
Galvanic barrier between
DOM and backbone cable

## Slide 25: Summary
Reliable calculation model for KM3NeT power system available
Components have been defined
KM3NeT-Fr (38 km off-shore)
  AC upto the base of the Detection Unit
  Main cable delivered and ready for deployment
KM3NeT-It (100 km off-shore)
  DC only
  Existing network being expanded
KM3NeT-Gr (<30 km off-shore)
  Design will be similar to that of KM3NeT-Fr

## Slide 26: Acknowledgement
I would like to thank my colleagues in the KM3NeT collaboration;
Rosanna Cocimano, Angelo Orlando and Riccardo Pappaleo of LNS/INFN, Stephane Theraube, Jean-Jacques Destelle and Patrick Lamare of CPPM,
Paul Timmer of Nikhef
for all their interactions on this subject. (… and everybody I forgotten)
The pictures shown in this paper are from several presentations given in the KM3NeT collaboration meetings.